## Instructions
Asset Health Index (AHI) Matrix
The AHI Matrix is a tool which attempts to quantify the current health and future life expectancy of a given asset. The health and remaining useful life expectancy is based on the synthesis of various available condition monitoring data into a single indicator of overall system life, leveraging certain weightings and approaches to combine multiple data sets into one “figure of merit”, the Overall Asset Health Index”.
Significant Components of the Matrix
Condition Indicators: CI’s may be essential components or elements of the asset which require maintenance of some kind, or are derived from condition assessments, whether by a human or by sensors or both, that can be used to assess the health of an asset or key element (sub component) of an asset.
Failure Mode Impact Weighting: a number, 1 through 10 which determines the significance of each CI when compared to other CI’s derived from the same asset. A score of 10 means the respective CI is most significant. An appropriate weighting is determined by reviewing the Severity or Effect Definition tables that have been provided and are located below the AHI Matrix.
Test Result Data: some technologies (e.g. oil testing & vibration) will have separate programs which generate (a numerical value indicative of the condition of the test item using the vendors own scoring system) an output score; this score can be placed into the Tests Result Data section of the Matrix. The tool will use the score to calculate an AHI score, using the selected Impact Weighting, for the relevant CI. (Note: The Test Result Data section is also used by the tool when CI information is derived from the tables, in these instances; data from other programs were not available for use).
CI “Normalized” Condition Factor (CF): This is a score, 0 through 4 (0 = poor condition, 4 = excellent condition) used to determine the current condition of the asset element/component.
Use of tables to determine an appropriate factor: When the CI in the Matrix is highlighted light green, the CI Normalized Condition Factor score is derived by selecting the most appropriate explanation of known CI conditions from the Condition Indicator tables below the Matrix and applying the score associated with it. (See screen shot further below)
If the CI in the Matrix is not highlighted light green, use the Normalized Condition Factors Definition Tables to determine an appropriate CI factor to be manually entered into the Matrix. (See screen shot further below).
Level 0 through Level 4 Indicators: this section provides a visual aid as to the calculated condition of each CI. This visual aid is determined by the CI Normalized Condition Factor, each level is assigned a score to be used in the AHI calculation, the visual aids and scores are as follows:
| Level | Level 4 | Level 3 | Level 2 | Level 1 | Level 0
| Visual | Excellent | Acceptable | Unusual | Abnormal | Poor
(Critical CI) Low Asset Health Alert: This section provides an alert when an individual CI which has a weighting of 8 or higher is at a level 1 or level 0 condition.
Individual CI Health Monitor: This is the calculated health score for each CI shown as a percentage. This section also serves to provide visual aids and reminders where errors occur in the matrix.
Overall Asset Health Index
The final condition indication for the asset being scored, rolling up all the sub component and/or different condition measurements, is given at the bottom right corner of the Matrix.
Overall Asset Health Index: is shown as a percentage and is calculated from the sum of all CI scores (CF x Weighting) and the sum of all max scores. Weightings are calculated automatically from a "pool" of 100 points, therefore the sum of all weightings will always equal 100.
Confidence Factor: shown as a percentage this allows the user to determine the effectiveness of the Overall AHI based on the amount of data analyzed compared to the amount of data available in the Matrix.
Projected Remaining Useful Life: When the “Asset Acquired” date & the original “Estimated Life” are entered (at the top of the Matrix) the tool will place an estimate of the remaining useful life based on the current Overall AHI. This is based on a simple proportioning of the amount of remaining useful life given the current state of the asset as indicated by the single overall asset health Index score.
Potential Useful Life Lost: as with the projected remaining useful life, when information is entered regarding the acquired date and original estimated life expectancy, the tool will predict useful life lost due to current asset health.
How to Use the Tool
The tool is password protected to preserve the asset component/element descriptions, all the calculations, condition indicator tables and pre-determined weightings.
All appropriate Condition Indicators will have been entered into the Matrix, and appropriate Failure Mode Impact Weightings applied. Where an individual asset element could have multiple conditions to consider it will be found in the Condition Indicator Tables, this brings some consistency to evaluating the more “complex” CI’s.
Any cell which is highlighted yellow requires a manual data entry; these should only be in un-protected cells both in the Matrix and the Condition Indicator Tables, yellow highlighted cells in protected areas of the Matrix should be reported to AM for review.
If the date is known when the asset was first put into service it should be entered at the top of the Matrix. Also required (if available) is the originally predicted (warranted / promised) life expectancy of the asset.
When the asset is being inspected particular attention should be paid to the Condition Indicators listed in the Matrix, then an appropriate CI Factor can be applied dependent on actual findings.
The CI Normalized Condition Factor is determined by either:
Selecting the most appropriate explanation of current conditions from the selection in the Condition Indicator Tables, and assigning the applicable number,
Or, determining which of the definitions is most accurate in the Normalized Condition Factors Definitions Table and inserting this number into the Matrix.
Note: when the CI in the Matrix is highlighted light green, the Condition Indicator Tables are used for this scoring.
As much data should be entered into the Matrix as possible to ensure the most accurate determination of current asset condition.
When using the tool, if a particular CI listed in the Matrix is not relevant/applicable to the asset being inspected it can be disregarded by the tool for determining asset health by entering a “0” in the Failure Mode Impact Weighting section for the relevant CI. It is important to do this to ensure the confidence factor remains accurate. This function should not be used to remove relevant CI's as it will artificially affect the confidence factor.
The Individual CI Health Monitor section (far right column) identifies incorrect or missing data entries.
The tool will do the rest.

## Motors
Plant Name | Harding Street | Unit Name | Unit 7 | Unit ID | 7
Parent Asset ID |  | Parent Asset Name |  | Parent Asset Type | Damper |  | Asset Sub Type | ID Fan
Asset ID | DEFG-3434 | Asset Name | Fan Motor
| Notes: a. The yellow highlighted cells require data entry. b. The green highlighted Condition Indicators are listed in a table below where Condition Factors, Failure Modes & Weightings can be determined. c. If data is left blank, in the "Normalized Condition Factor" column (F) then the associated condition indicator is not used in the scoring process. d. The scoring for each condition indicator is 0 thru 4. 0 = very poor health, 4 = good health. |  | The weighting factor for each CI. 1 = low. 10 = high. Can be used as a "switch" to withdraw a CI from the calculations - enter "0" Missing data returns yellow highlighted cell. | Oil: 4 = severe. 3 = significant. 2 = moderate. 1 = minor. 0 = ok. Vibration: 1 = critical. 2 = significant. 3 = minor. 4 = ok. Missing data returns yellow highlighted cell. | The actual condition of the condition indicator. On a scale of 0 (Poor) thru 4 (Excellent). Blank = No input. 0 = Level 0 (Poor). 1 = Level 1 (Abnormal). 2 = Level 2 (Unusual). 3 = Level 3 (Acceptable). 4 = Level 4 (Excellent). Missing data returns yellow highlighted cell.
[10 empty] | Insert Asset Acquired Date in the following format: mm/dd/yy |  | Insert Estimated Life as a number in years. | If "0" weighting in column (D) is entered = N/A. | This value for the Overall Asset Health Index is used to trigger flags when it is reached and to provide an "Intervention" output for other program use.
Date of Record: | 2014-09-23 14:30 | Asset Health Matrix for | 7 - 1 ID Fan Motor |  |  |  | Serial No. | 2709AB-01 |  | Asset Acquired | 2005-02-01 | Estimated Life (yrs) | 40 | 40 | Overall AHI Poor Health Set Point | Sum | Level 0 Forcing | Level 1 Forcing | Sum | Max CF | Pool 100 | Forcing Trigger |  |  |  |  | Health Risk Outputs
Rev 1. Oct 2014 |  |  | (1 - 10) |  | (0 - 4) |  |  |  | Individual CI Health |  |  |  | Individual CI Health Monitor | Notes |  | 297.1154 | 0.6 | 0.3 | 400 | 4 | 100 | 8 | Error Reporting |  | 25 | 17 | 0 | 0 | 0
Technology or Procedure | Condition Indicator (CI) | Failure Mode (s) | Failure Mode Impact Weighting | Test Result Data | CI "Normalized" Condition Factor (CF) |  | Level 4 | Level 3 | Level 2 | Level 1 | Level 0 | (Critical CI) Low Asset Health Alert |  |  |  | CI score | Calc for Level 1 & 0 Forcing | Switch for Level 1 & 0 Forcing | Total Max | Max CI score | Weighting (Auto) | Weighting adjustment | Is Column "F" blank | CF entry errors | Confidence Factor |  | Individual CI's Health Risk flagged = 1 | AHI Intervention flagged =1 | CI Health Monitor flagged = 1 | Original FM Weightings
Re-name or assign Technology or Procedure categories | Insert all Relevant CI's for this Asset | Provide brief Failure Mode description for each CI | Assign FM Weighting - use table below for reference | Used only for actual condition data from a 3rd party program | Assign CI Factor only if asset is currently being assessed | Enter "X" if CI requires assigning to tables below | [7 empty] | This section is for AM and / or the user to add notes if deemed to be useful.
Oil Analysis | Drive End Bearing Oil | Contaminated Oil | 3 | 2 | 2 |  |  |  | Unusual |  |  | N/A | 50% | Moderate particle count and 8 mils vibration at 806 RPM |  | 5.7692 | 1 | 0 | 11.5385 | 11.5385 | 2.8846 | 3 | 1 | 0 | 1 | 1 | 0 | 0 | 0 | 3
| Non Drive End Bearing Oil | Contaminated Oil | 3 | 1 | 3 |  |  | Acceptable |  |  |  | N/A | 75% | Changed oil in IB bearing |  | 8.6538 | 1 | 0 | 11.5385 | 11.5385 | 2.8846 | 3 | 1 | 0 | 1 | 1 | 0 |  | 0 | 3
|  |  | 0 | [8 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | [8 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | [8 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
Vibration Analysis | Drive End Bearing | Component Fatigue Failure | 5 | 3 | 3 |  |  | Acceptable |  |  |  | N/A | 75% |  |  | 14.4231 | 1 | 0 | 19.2308 | 19.2308 | 4.8077 | 5 | 1 | 0 | 1 | 1 | 0 |  | 0 | 5
| Non Drive End Bearing | Component Fatigue Failure | 5 | 3 | 3 |  |  | Acceptable |  |  |  | N/A | 75% |  |  | 14.4231 | 1 | 0 | 19.2308 | 19.2308 | 4.8077 | 5 | 1 | 0 | 1 | 1 | 0 |  | 0 | 5
|  |  | 0 | [8 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | [8 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | [8 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
Internal Inspection & Measurements | Drive End Bearing Condition | Bearing failure / Overheating | 7 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 28.8462 | 1 | 0 | 38.4615 | 38.4615 | 9.6154 | 10 | 1 | 0 | 1 | 1 | 0 |  | 0 | 7
| Non Drive End Bearing Condition | Bearing failure / Overheating | 7 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 28.8462 | 1 | 0 | 38.4615 | 38.4615 | 9.6154 | 10 | 1 | 0 | 1 | 1 | 0 |  | 0 | 7
| Electrical Bolted Connections | Overheating / Failure / Explosion | 7 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 28.8462 | 1 | 0 | 38.4615 | 38.4615 | 9.6154 | 10 | 1 | 0 | 1 | 1 | 0 |  | 0 | 7
| Stator Condition | Loose winding / Pd / Potential Failure | 8 | - |  | x | [5 empty] | N/A | Enter CF # |  |  | - | 1 | 1 | - | - | - | - | 0 | Enter CF # | 1 | 0 | 0 |  | 0 | 8
| Rotor Condition | Loose Winding / Shorted Turns | 8 | - |  | x | [5 empty] | N/A | Enter CF # |  |  | - | 1 | 1 | - | - | - | - | 0 | Enter CF # | 1 | 0 | 0 |  | 0 | 8
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
External Inspections & Observations | Drive End Bearing Temp. | Low/Dirty Lubricant / Bearing Failure | 4 | - | 3 |  |  | Acceptable |  |  |  | N/A | 75% | Observation from PI |  | 11.5385 | 1 | 0 | 15.3846 | 15.3846 | 3.8462 | 4 | 1 | 0 | 1 | 1 | 0 |  | 0 | 4
| Non Drive End Bearing Temp. | Low/Dirty Lubricant / Bearing Failure | 4 | - | 3 |  |  | Acceptable |  |  |  | N/A | 75% | Observation from PI |  | 11.5385 | 1 | 0 | 15.3846 | 15.3846 | 3.8462 | 4 | 1 | 0 | 1 | 1 | 0 |  | 0 | 4
| Coupling Alignment | Vibration / Over Heated Bearings | 4 | - | [7 empty] | N/A | Enter CF # |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 1 | 0 | 0 |  | 0 | 4
| Anti Condensation Heaters | Moisture in Windings | 3 | - | [7 empty] | N/A | Enter CF # |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 1 | 0 | 0 |  | 0 | 3
| Bearing Housing Breathers | Over Pressurized Housings/Oil Leaks | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Winding Temperatures | Overheating / Failure | 8 | - | 3 |  |  | Acceptable |  |  |  | N/A | 75% | Observation from PI |  | 43.2692 | 1 | 1 | 57.6923 | 57.6923 | 14.4231 | 15 | 1 | 0 | 1 | 1 | 0 |  | 0 | 8
| Audible Test (Does it sound OK) | Internal Electrical Fault / Bearings | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Coupling Guard | Personnel Safety / Coupling Damage | 1 | - | [7 empty] | N/A | Enter CF # |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 1 | 0 | 0 |  | 0 | 1
| Foundation / Holding Down Bolts | Soft Foot / Vibration / Alignment Issues | 4 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 11.5385 | 1 | 0 | 15.3846 | 15.3846 | 3.8462 | 4 | 1 | 0 | 1 | 1 | 0 |  | 0 | 4
| Drive Coupling, Belts and Pulleys | Broken Drive / Failed Belts / Vibration | 6 | - |  | x | [5 empty] | N/A | Enter CF # |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 1 | 0 | 0 |  | 0 | 6
| Cooler Condition / Air Filters / Fan | High Winding / High Bearing Temps. | 3 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 8.6538 | 1 | 0 | 11.5385 | 11.5385 | 2.8846 | 3 | 1 | 0 | 1 | 1 | 0 |  | 0 | 3
| Grounding | Fault Protection Inadequate | 2 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 5.7692 | 1 | 0 | 7.6923 | 7.6923 | 1.9231 | 2 | 1 | 0 | 1 | 1 | 0 |  | 0 | 2
| Brushgear | Dirty / Sparking - Potential Failure | 0 | - |  | x | [5 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Lubricant Oil/Grease Condition | Bearing failure / Overheating | 4 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 11.5385 | 1 | 0 | 15.3846 | 15.3846 | 3.8462 | 4 | 1 | 0 | 1 | 1 | 0 |  | 0 | 4
IR Thermography | Drive End Bearing | Overheated Bearing | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Non Drive End Bearing | Overheated Bearing | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Motor Connections | High Temp. / Loose Connections / Failure | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Motor Casing | Winding Hotspot / Partial Discharge | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Brushgear - Sliprings | Overheating - Failure | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
Visual Examination |  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
Other Technology or Procedure |  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
Other Technology or Procedure |  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
Other Technology or Procedure |  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
Cognizant Personnel | Subject Matter Expert Evaluation | Overall Motor Experience | 8 | - | 3 |  |  | Acceptable |  |  |  | N/A | 75% |  |  | 43.2692 | 1 | 1 | 57.6923 | 57.6923 | 14.4231 | 15 | 1 | 0 | 1 | 1 | 0 |  | 0 | 0
| External General Condition | Dirty Cooling Fins / Fan / Breathers | 2 | - | 3 |  |  | Acceptable |  |  |  | N/A | 75% |  |  | 5.7692 | 1 | 0 | 7.6923 | 7.6923 | 1.9231 | 2 | 1 | 0 | 1 | 1 | 0 |  | 0 | 0
| Asset Age | Age Effect on Reliability | 5 | - | 3 |  |  | Acceptable |  |  |  | N/A | 75% |  |  | 14.4231 | 1 | 0 | 19.2308 | 19.2308 | 4.8077 | 5 | 1 | 0 | 1 | 1 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
Motor Tests | PdMA Off line Tests | Moisture / Winding Failure | 4 | - | [7 empty] | N/A | Enter CF # |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 1 | 0 | 0 |  | 0 | 4
| PdMA On line Tests | Moisture / Winding Failure | 4 | - | [7 empty] | N/A | Enter CF # |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 1 | 0 | 0 |  | 0 | 4
| Partial Discharge Testing (=>4kV) | Pd / Spark Erosion / Insulation Failure | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Electromagnetic Interference Testing | Pd / Spark Erosion / Insulation Failure | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Electrical Testing | Moisture / Winding Failure | 0 | - |  | x | [5 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
| Power Supply (high/low/balanced) | Overheating Windings / Trip on Start | 0 | - |  | x | [5 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 0
Cognizant Personnel |  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 8
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 2
|  |  | 0 | - | [7 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 5
Asset Health Index/Residual Life Factors | 10% | 15% | 20% | 25% | 30% |  | 35% | 0 |  | Overall Asset Health Index | 74.2788 | % | Potential Useful Life Lost |  | If Overall Asset Health Index is highlighted Red, Intervention is required.
Residual Life Factors | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 |  | 0.45 |  |  | Data Availability (Confidence Factor) | 68 | % | 15.5 | %
0.8 | [9 empty] | Projected Remaining Useful Life | 24.8 | Yrs | 6.2 | yrs
40% | 50% | 60% | 70% | 80% | 90% |  | 100% |  |  |  |  | Consider Collecting More Data
0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 0.95 |  | 1 | 1 | [5 empty] | Max Value
|  |  | 0.8 |  |  |  |  | 1 |  |  |  |  | 74.2788 | 100
Current Asset Health Index | 74.2788 | [11 empty] | Donut | Needle
Physical Life Consumed | 22.5% | 9 | Years | [9 empty] | 180 | 0 | 0
Remaining Physical Life | 77.5% | 31 | Years | [9 empty] | 45 | 0.69091 | 0.72294
Estimated Useful Life Remaining | 62% | 24.8 | Years | [9 empty] | 45 | 0 | 0
Current Date | 2014-09-23 14:30 | Original Estimated Total Life | 40 | [9 empty] | 45 | Health Threshold
Asset Acquired | 2005-02-01 | [11 empty] | 45 | 0 | 0
[14 empty] | -0.30902 | 0.95106
[14 empty] | 0 | 0
C.I. Normalized Condition Factors | Description | Normalized Condition Factors Definition
0 | Poor | Condition is bad, prompt repair/rectification is required, operation is not advised.
1 | Abnormal | Possible early signs of a failure that requires repair/rectification at earliest opportunity.
2 | Unusual | Not typical but does not necessarily indicate a possible failure, extra monitoring warranted, repair/rectification at convenient opportunity.
3 | Acceptable | Includes everyday wear and tear and other minor incidents that are viewed as not unusual.
4 | Excellent | Equipment in top condition, with insignificant wear and tear.
Failure Mode Impact Weighting 1 = Low, 10 = High | Description | Severity or Effect Definition
10 | Highest | Failure Severity: Catastrophic, asset becomes inoperable, the failure may result complete unsafe operation and possible fatalities. Significant financial loss or irreversible severe environmental damage that violates law or regulation.
Influence on total asset health: Has the highest impact, important data necessary for determining the most reliable, efficient and safe operation.
9 | Extremely High | Failure Severity: Large reduction in safety margin, asset becomes inoperable; failure may result in LTI's or recordables or reversible environmental damage causing a violation of law or regulation.
Influence on total asset health: Would have an extremely high impact, important data necessary for determining high levels of reliability, efficiency and safety.
8 | Very High | Failure Severity: Failure renders the asset inoperable or unfit for use, reduces the capability of the system or the operators to cope with adverse operating conditions to the extent that there would be significant reduction in safety margin or functional capability.
Influence on total asset health: Would have a very high impact on reliability or for the asset to operate safely, efficiently or correctly.
7 | High | Failure Severity: Has the potential to cause the asset to be inoperable temporarily, causes significant increase in operator workload, causes significant customer dissatisfaction.
Influence on total asset health: Would have a high impact on reliability or for the asset to operate safely, efficiently or correctly.
6 | Moderate | Failure Severity: Failure results in a subsystem or partial malfunction of the asset, reduction in safety margins, conditions impairing operator efficiency or creating significant discomfort.
Influence on total asset health: Would have a moderate impact on reliability or for the asset to operate safely, efficiently or correctly.
5 | Low | Failure Severity: Failure creates enough of a performance loss to cause light damage or minor injuries and possible customer complaints; slight reduction in safety margin or functional capabilities.
Influence on total asset health: Would have a low impact on reliability or for the asset to operate safely, efficiently or correctly.
4 | Very Low | Failure Severity: Failure can be overcome with modifications to the process or asset, but there is minor performance loss.
Influence on total asset health: Would have a very low impact on reliability or for the asset to operate safely, efficiently or correctly.
3 | Minor | Failure Severity: Failure would create a minor nuisance which can be overcome without performance loss.
Influence on total asset health: Would have a minor impact on reliability or for the asset to operate safely, efficiently or correctly.
2 | Very Minor | Failure Severity: Very minor, no damage, no injuries, only results in a maintenance action (only noticed by discriminating customers)
Influence on total asset health: Contributes to minor improvements in reliability, efficiency or safety.
1 | Negligible | Failure Severity: No relevant effect on reliability or safety.
Influence on total asset health: Only minimal effect on improvements in reliability, efficiency or safety.
Assign Failure Mode Impact Weightings 1 = Low, 10 = High | Choose the Condition Indicator Factor that best describes actual equipment condition | C.I. Normalized Condition Factors 0 = Poor , 4 = Excellent | Condition Indicators
"0" = omit from AHI | Enter one number (0 - 4) | (0 - 4) | For each CI list all possible conditions ranging from very poor to excellent health. (0 - 4)
7 |  |  | Drive End Bearings
7 | 3 | 0 | Excessive cracks on bearing races/shells with significant propagation should be repaired promptly.
|  | 0 | Individual spalls (fatigue failure) either isolated or associated with cracking, that extend over a significant area as well as multiple spalls of appreciable size - repair promptly.
|  | 1 | Significant spalling or surface peeling of bearing races, rollers or Babbitt indicates a failure in process.
|  | 1 | Micro-pitting or flaking of the bearing rollers, in particular at the shoulders, may indicate the onset of failure.
|  | 1 | Obvious cracks on bearing races/shells are a failure, repair/replacement should be scheduled.
|  | 1 | Oil slinger ring cracked or damaged
|  | 1 | Bearing Corrosion: Red/brown areas on balls, race-way, cages or shells where subject to corrosion by water, acids, and other agents.
|  | 1 | Bearing Misalignment: A frequent source of trouble resulting in overheating and separator failure. Common causes are bent shafts, out-of-square shaft shoulders, out-of-square spacers, and out-of-square clamping nuts.
|  | 2 | Overheating: Bearing surfaces blue/brown. Temperatures in excess of 400F can anneal bearing surfaces.
|  | 2 | Excessive bearing roller end wear - signifies excess side loading.
|  | 2 | Electrical Damage (Fluting): When electric currents pass through a bearing, there is arcing and burning at the points between the races and the rolling elements or the journal and Babbitt area, where the current jumps the air gap.
|  | 2 | Vibration Brinell (False Brinell): Caused by the rapid movement of the balls in the raceway while the equipment is idle.
|  | 2 | Uneven wear pattern on bottom shell of Babbitt bearing, signifying misalignment or uneven loading.
|  | 2 | Bearing pedestal grounding missing or contaminated with oil / grease / debris.
|  | 2 | Wear marks on top shell of Babbitt bearing, signifying incorrect clearances, misalignment or excessive vibration.
|  | 3 | Circumferential visual marks or lines on bearing races or Babbitt, possibly due to soft particle wiping or staining.
|  | 3 | Bearing operating at an appropriate temperature and not noisy, no significant vibration.
|  | 3 | Isolated small indentations or nicks on race or Babbitt surfaces.
|  | 4 | Bearing in top condition no signs of degradation or cause for concern.
7 |  |  | Non Drive End Bearings
7 | 3 | 0 | Excessive cracks on bearing races/shells with significant propagation should be repaired promptly.
|  | 0 | Individual spalls (fatigue failure) either isolated or associated with cracking, that extend over a significant area as well as multiple spalls of appreciable size - repair promptly.
|  | 1 | Significant spalling or surface peeling of bearing races, rollers or Babbitt indicates a failure in process.
|  | 1 | Micro-pitting or flaking of the bearing rollers, in particular at the shoulders, may indicate the onset of failure.
|  | 1 | Oil slinger ring cracked or damaged
|  | 1 | Obvious cracks on bearing races/shells are a failure, repair/replacement should be scheduled.
|  | 1 | Bearing Corrosion: Red/brown areas on balls, race-way, cages or shells where subject to corrosion by water, acids, and other agents.
|  | 1 | Bearing Misalignment: A frequent source of trouble resulting in overheating and separator failure. Common causes are bent shafts, out-of-square shaft shoulders, out-of-square spacers, and out-of-square clamping nuts.
|  | 2 | Overheating: Bearing surfaces blue/brown. Temperatures in excess of 400F can anneal bearing surfaces.
|  | 2 | Excessive bearing roller end wear - signifies excess side loading.
|  | 2 | Electrical Damage (Fluting): When electric currents pass through a bearing, there is arcing and burning at the points between the races and the rolling elements or the journal and Babbitt area, where the current jumps the air gap.
|  | 2 | Vibration Brinell (False Brinell): Caused by the rapid movement of the balls in the raceway while the equipment is idle.
|  | 2 | Uneven wear pattern on bottom shell of Babbitt bearing, signifying misalignment or uneven loading.
|  | 2 | Bearing pedestal grounding missing or contaminated with oil / grease / debris.
|  | 2 | Wear marks on top shell of Babbitt bearing, signifying incorrect clearances, misalignment or excessive vibration.
|  | 3 | Circumferential visual marks or lines on bearing races or Babbitt, possibly due to soft particle wiping or staining.
|  | 3 | Bearing operating at an appropriate temperature and not noisy, no significant vibration.
|  | 3 | Isolated small indentations or nicks on race or Babbitt surfaces.
|  | 4 | Bearing in top condition no signs of degradation or cause for concern.
7 |  |  | Electrical Connections
7 | 3 | 0 | Cable lug or connector severely discolored/disfigured due to overheating
|  | 0 | Connecting bolted hardware loose or missing
|  | 0 | Cable insulation chaffing on grounded surface, showing signs of arcing or partial discharge
|  | 0 | Terminal box cover missing
|  | 1 | Cable lug shows signs of overheating, blue/brown color
|  | 1 | Dissimilar metals - signs of corrosion activity
|  | 1 | Terminal box cover loose or poor/missing gasket
|  | 1 | Electrical testing of contact resistance records greater than 15 Micro-ohms per any single connection (at 10 amps test current)
|  | 2 | Cable lug deformed, only partial contact with connector, no discoloration
|  | 2 | Insufficient/inappropriate bolting hardware
|  | 2 | Cable insulation chaffing on grounded surfaces, or on different phase conductor - no signs of arcing.
|  | 2 | Terminal box cover bolting hardware missing or loose.
|  | 3 | Cable lugs/connector displaying signs of oxidizing (age) but not overheating. Bolting hardware tight and appropriate.
|  | 3 | Electrical testing of contact resistance records less than 15 Micro-ohms per any single connection (at 10 amps test current)
|  | 4 | All electrical connections are in top condition, all bolting hardware is tight, good surface area contact on all flexibles, electrical testing reveals all connections below 10 Micro-ohms (at 10 amps test current)
8 |  |  | Stator
8 |  | 0 | Stator winding slot wedges loose or missing
|  | 0 | End blocking missing, loose or ineffective
|  | 0 | "Rub" damage on stator winding.
|  | 1 | Stator winding end blocking loose
|  | 1 | Significant dirt/debris on winding or core, possibly blocking cooling paths
|  | 1 | Stator winding partial discharge evidence on winding insulation or grounded/insulated surfaces
|  | 1 | "Rub" damage on stator core
|  | 2 | Slightly damaged insulation on winding - no Pd present.
|  | 2 | Slight Dirt/debris on windings and/or core
|  | 2 | Oil/grease on windings
|  | 3 | Windings show no significant Pd, mostly clean with little or no oil/grease present. All locating hardware is present and secure.
|  | 4 | Windings are dry and free from dirt & debris with no signs of Pd or chaffing. Windings are held securely in place.
8 |  |  | Rotor
8 |  | 0 | Rotor bar slot wedges loose or missing
|  | 0 | Cooling fan damaged or loose
|  | 0 | Rotor end shield damaged/loose, or signs of partial discharge/arcing.
|  | 0 | "Rub" damage on rotor winding.
|  | 1 | Deep scoring or discolored surface on bearing journals signifies early bearing failure.
|  | 1 | "Rub" damage on rotor core
|  | 2 | Slight abrasion on bearing journals.
|  | 2 | Rotor not on magnetic center
|  | 2 | Rotor air gap not concentric
|  | 2 | Shaft seal clearance inadequate
|  | 3 | Circumferential visual marks or lines on journals, possibly due to soft particle wiping or staining.
|  | 3 | Isolated small indentations or nicks on journal surfaces.
|  | 3 | Rotor shows no significant mechanical damage or electrical Pd activity. All locating hardware is present and secure.
|  | 4 | Windings/rotor bars are dry and free from dirt & debris with no signs of Pd or chaffing. Windings are held securely in place.
4 |  |  | Foundation Integrity / Hold Down Bolts
4 | 3 | 0 | Significant faults/cracks in foundation making hold down hardware ineffective.
|  | 0 | Grout broken away and shims either missing or loose, hold down hardware ineffective. (on all feet)
|  | 1 | Grout broken away and shims either missing or loose, hold down hardware ineffective. (on 1 or 2 feet only)
|  | 2 | Foundation is sound, grouting falling away but shims tight and hold down hardware tight.
|  | 3 | Foundation is sound but grouting may be showing signs of cracking. All hold down hardware intact and secure, shims still effective.
|  | 4 | Foundation is sound, grouting is sound all hold down hardware intact and secure, shims effective.
6 |  |  | Drive Coupling / Belts & Pulleys
6 |  | 0 | Drive pulley cracked or otherwise damaged significantly
|  | 0 | Coupling bolts loose or missing
|  | 1 | Drive pulley showing signs of abnormal wear - affecting belt wear
|  | 1 | Drive belts require significant adjustment (tension and/or alignment issue)
|  | 1 | Drive belts badly worn/fraid/missing
|  | 1 | Coupling assembly hardware or grease in poor state (missing, loose, contaminated)
|  | 1 | Coupling alignment requires significant adjustment
|  | 2 | Drive belts require minor adjustment (all in place but tension/alignment slightly out)
|  | 3 | Drive belts showing normal signs of wear alignment and tension appear good.
|  | 3 | Coupling alignment appears good, all hardware in place and tight, grease in good condition.
|  | 4 | All belts in place correctly aligned and tensioned
|  | 4 | Coupling correctly aligned, all bolts in place and tight, all hardware in place, grease in good condition.
3 |  |  | Coolers
3 | 3 | 0 | Coolers blocked
|  | 0 | Water coolers leaking water into motor
|  | 1 | Air filter dp alarm active
|  | 1 | Air filters very dirty
|  | 2 | Air filters missing or dirty
|  | 3 | Air filters in place, in good condition. Coolers operating at normal temperature.
|  | 3 | Cooler water system fully functional and operating at normal pressure and temperature
|  | 4 | Cooler assembly fully functional at correct pressure / temperature and known to be clean internally with no defects.
2 |  |  | Grounding
2 | 3 | 1 | Motor ground strap/conductor missing or incorrect conductor size/type.
|  | 2 | Motor ground strap/conductor - poor connection to motor or ground.
|  | 3 | Motor ground strap/conductor in place and good electrical contact at motor and ground.
|  | 4 | Motor ground strap/conductor in place, correct size, secured in the most appropriate fashion and good electrical contact at motor and ground.
5 |  |  | Brushgear
0 |  | 0 | Severe arcing at the brushgear during operation
|  | 0 | Slip rings badly scored or burnt
|  | 0 | Loose brush connecting wires, or bus connections
|  | 0 | Brushes worn down to the point where brush springs are not being effective
|  | 1 | Brushes worn down - spring only just maintaining contact with brush
|  | 1 | Slip rings showing signs of arcing or brush chatter
|  | 1 | Enclosure contaminated with large amount of carbon dust and/or oil
|  | 2 | Brushes beginning to wear down - spring still in full contact with brush
|  | 2 | Uneven wear on brush contact area suggesting spring tension issues
|  | 3 | Slip rings, brushes and hardware in normal condition with minimal dust/oil present
|  | 4 | Brushgear assembly is free from dirt / oil, with correctly tensioned full length brushes in place. All hardware in top condition.
4 |  |  | Lubrication
4 | 3 | 0 | No visible sign of oil in the oil reservoir
|  | 0 | Oil leaks from cracks in the bearing housing require prompt attention.
|  | 1 | Low oil/grease levels, below recommended levels.
|  | 1 | Black oil (old degraded viscosity)
|  | 1 | Grease has become "thin" due to overheating
|  | 1 | Debris &/or particles in the oil/grease.
|  | 1 | Incorrect lubricant
|  | 1 | Metal particles picked up on a magnet in the filter housing or sump.
|  | 1 | Oil filter containing metal particles or "silver sludge" is a strong indication of a bearing failure.
|  | 2 | Oil leaking from the bearing housing via gasketed joints or fittings.
|  | 2 | Grease "oozing" from bearing housing/retainer.
|  | 2 | Leaking shaft seals (oil leaking out vs. debris entering housing).
|  | 3 | Oil/grease is of an appropriate viscosity and color and free from debris, no leaks
|  | 4 | Oil/grease in as new condition with no discoloration or signs of debris
4 |  |  | Electrical Testing
0 |  | 0 | Winding Insulation (Meggar) test result < 100MΩ (after 1 Minute) Failure mode: contamination, defects, and deterioration of ground insulation
|  | 0 | Winding resistance balance > 5%. Failure mode: broken and cracked windings, poor connections, shorted turns in winding.
|  | 0 | HiPot test failure
|  | 0 | Polarization Index (after 10 mins) < 1 or Dielectric Absorption Ratio (after 60 secs) < 1 Failure mode: contamination, defects, water ingress, and deterioration of ground insulation.
|  | 1 | Winding Insulation (Meggar) test result < 200MΩ (after 1 Minute) Failure mode: contamination, defects, and deterioration of ground insulation
|  | 1 | Polarization Index (after 10 mins) 1 - 2 or Dielectric Absorption Ratio (after 60 secs) 1 - 1.4 Failure mode: contamination, defects, water ingress, and deterioration of ground insulation.
|  | 1 | Winding resistance balance < 5% and >2%. Failure mode: broken and cracked windings, poor connections, shorted turns in winding.
|  | 2 | Winding Insulation (Meggar) test result > 200MΩ and < 500MΩ (after 1 Minute) Failure mode: contamination, defects, and deterioration of ground insulation
|  | 2 | Polarization Index (after 10 mins) > 2 or Dielectric Absorption Ratio (after 60 secs) > 1.4 Failure mode: contamination, defects, water ingress, and deterioration of ground insulation.
|  | 2 | Bearing insulation test failure < 5MΩ
|  | 2 | Winding resistance balance between 1 & 2%. Failure mode: broken and cracked windings, poor connections, shorted turns in winding.
|  | 2 | Shaft voltage test failure
|  | 3 | Polarization Index (not required if IR > 500MΩ)
|  | 3 | Winding Insulation (Meggar) test result > 500MΩ (after 1 Minute) Failure mode: contamination, defects, and deterioration of ground insulation
|  | 3 | Winding Resistance Balance around 1%. Failure mode: broken and cracked windings, poor connections, shorted turns in winding.
|  | 4 | All Electrical testing results demonstrate as new condition.
3 |  |  | Power Supply
0 |  | 2 | Supply Voltage (high/low) Maximum acceptable voltage variation 10% at rated frequency.
|  | 2 | Supply Voltage (un-balanced) Recommended maximum percentage un-balanced voltage is 1%. Above 5% un-balance is not recommended.
|  | 2 | On Load Current (amps) Should not vary more than 10% of nameplate.
|  | 2 | On Load Speed (rpm) Should not exceed 20% of the difference between synchronous speed and rated speed when measured at rated voltage, frequency and load.
|  | 3 | Power supply within acceptable limits
|  | 4 | Power supply at design / rated values, motor full load amps and speed at rated values.
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
Insert CI name here
0
0
0
0
1
1
1
1
1
1
1
2
2
2
2
2
2
2
3
3
3
3
3
3
3
4
4
50%
0% 100%
Asset Health Meter
Sum score = sum of scores from all submitted C.I's. Overall Asset Health Index = sum score / max score. <25. 25-50. 50-75. >75. Data availability = max score / max possible score. <60. 60-80. >80. When data availability falls below 75% = Consider Collecting More Data When any condition indicator has a "0" score = 1 or more CI in Poor Health When the projected asset life loss is >25% = Estimated > 1/4 Asset Life Lost
Note on I9: Russ: Enter Serial Number if this asset may be rotated with other identical assets, (spares, unit 1 to unit 2 etc.)
Note on L9: Russ: Enter the date this asset was first put into service - m/dd/yy
Note on N9: Russ: Enter the estimated life expectancy from first operating date.
Note on O9: Russ Cochran: Insert the minimum acceptable value for the Overall Asset Health Index, below this value the AHI will be flagged and an Intervention output is generated.