## Instructions
Asset Health Index (AHI) Matrix
The AHI Matrix is a tool which attempts to quantify the current health and future life expectancy of a given asset. The health and remaining useful life expectancy is based on the synthesis of various available condition monitoring data into a single indicator of overall system life, leveraging certain weightings and approaches to combine multiple data sets into one “figure of merit”, the Overall Asset Health Index”.
Significant Components of the Matrix
Condition Indicators: CI’s may be essential components or elements of the asset which require maintenance of some kind, or are derived from condition assessments, whether by a human or by sensors or both, that can be used to assess the health of an asset or key element (sub component) of an asset.
Failure Mode Impact Weighting: a number, 1 through 10 which determines the significance of each CI when compared to other CI’s derived from the same asset. A score of 10 means the respective CI is most significant. An appropriate weighting is determined by reviewing the Severity or Effect Definition tables that have been provided and are located below the AHI Matrix.
Test Result Data: some technologies (e.g. oil testing & vibration) will have separate programs which generate (a numerical value indicative of the condition of the test item using the vendors own scoring system) an output score; this score can be placed into the Tests Result Data section of the Matrix. The tool will use the score to calculate an AHI score, using the selected Impact Weighting, for the relevant CI. (Note: The Test Result Data section is also used by the tool when CI information is derived from the tables, in these instances; data from other programs were not available for use).
CI “Normalized” Condition Factor (CF): This is a score, 0 through 4 (0 = poor condition, 4 = excellent condition) used to determine the current condition of the asset element/component.
Use of tables to determine an appropriate factor: When the CI in the Matrix is highlighted light green, the CI Normalized Condition Factor score is derived by selecting the most appropriate explanation of known CI conditions from the Condition Indicator tables below the Matrix and applying the score associated with it. (See screen shot further below)
If the CI in the Matrix is not highlighted light green, use the Normalized Condition Factors Definition Tables to determine an appropriate CI factor to be manually entered into the Matrix. (See screen shot further below).
Level 0 through Level 4 Indicators: this section provides a visual aid as to the calculated condition of each CI. This visual aid is determined by the CI Normalized Condition Factor, each level is assigned a score to be used in the AHI calculation, the visual aids and scores are as follows:
| Level | Level 4 | Level 3 | Level 2 | Level 1 | Level 0
| Visual | Excellent | Acceptable | Unusual | Abnormal | Poor
(Critical CI) Low Asset Health Alert: This section provides an alert when an individual CI which has a weighting of 8 or higher is at a level 1 or level 0 condition.
Individual CI Health Monitor: This is the calculated health score for each CI shown as a percentage. This section also serves to provide visual aids and reminders where errors occur in the matrix.
Overall Asset Health Index
The final condition indication for the asset being scored, rolling up all the sub component and/or different condition measurements, is given at the bottom right corner of the Matrix.
Overall Asset Health Index: is shown as a percentage and is calculated from the sum of all CI scores (CF x Weighting) and the sum of all max scores. Weightings are calculated automatically from a "pool" of 100 points, therefore the sum of all weightings will always equal 100.
Confidence Factor: shown as a percentage this allows the user to determine the effectiveness of the Overall AHI based on the amount of data analyzed compared to the amount of data available in the Matrix.
Projected Remaining Useful Life: When the “Asset Acquired” date & the original “Estimated Life” are entered (at the top of the Matrix) the tool will place an estimate of the remaining useful life based on the current Overall AHI. This is based on a simple proportioning of the amount of remaining useful life given the current state of the asset as indicated by the single overall asset health Index score.
Potential Useful Life Lost: as with the projected remaining useful life, when information is entered regarding the acquired date and original estimated life expectancy, the tool will predict useful life lost due to current asset health.
How to Use the Tool
The tool is password protected to preserve the asset component/element descriptions, all the calculations, condition indicator tables and pre-determined weightings.
All appropriate Condition Indicators will have been entered into the Matrix, and appropriate Failure Mode Impact Weightings applied. Where an individual asset element could have multiple conditions to consider it will be found in the Condition Indicator Tables, this brings some consistency to evaluating the more “complex” CI’s.
Any cell which is highlighted yellow requires a manual data entry; these should only be in un-protected cells both in the Matrix and the Condition Indicator Tables, yellow highlighted cells in protected areas of the Matrix should be reported to AM for review.
If the date is known when the asset was first put into service it should be entered at the top of the Matrix. Also required (if available) is the originally predicted (warranted / promised) life expectancy of the asset.
When the asset is being inspected particular attention should be paid to the Condition Indicators listed in the Matrix, then an appropriate CI Factor can be applied dependent on actual findings.
The CI Normalized Condition Factor is determined by either:
Selecting the most appropriate explanation of current conditions from the selection in the Condition Indicator Tables, and assigning the applicable number,
Or, determining which of the definitions is most accurate in the Normalized Condition Factors Definitions Table and inserting this number into the Matrix.
Note: when the CI in the Matrix is highlighted light green, the Condition Indicator Tables are used for this scoring.
As much data should be entered into the Matrix as possible to ensure the most accurate determination of current asset condition.
When using the tool, if a particular CI listed in the Matrix is not relevant/applicable to the asset being inspected it can be disregarded by the tool for determining asset health by entering a “0” in the Failure Mode Impact Weighting section for the relevant CI. It is important to do this to ensure the confidence factor remains accurate. This function should not be used to remove relevant CI's as it will artificially affect the confidence factor.
The Individual CI Health Monitor section (far right column) identifies incorrect or missing data entries.
The tool will do the rest.

## Motors
Plant Name | Petersburg | Unit Name | PETE 1 | Unit ID | 1
Parent Asset ID | 202BI00000 | Parent Asset Name | Boiler Internals | Parent Asset Type | Boiler |  | Asset Sub Type | Tubes
Asset ID | 202BIHDWW0 | Asset Name | Waterwall
| Notes: a. The yellow highlighted cells require data entry. b. The green highlighted Condition Indicators are listed in a table below where Condition Factors, Failure Modes & Weightings can be determined. c. If data is left blank, in the "Normalized Condition Factor" column (F) then the associated condition indicator is not used in the scoring process. d. The scoring for each condition indicator is 0 thru 4. 0 = very poor health, 4 = good health. |  | The weighting factor for each CI. 1 = low. 10 = high. Can be used as a "switch" to withdraw a CI from the calculations - enter "0" Missing data returns yellow highlighted cell. | Oil: 4 = severe. 3 = significant. 2 = moderate. 1 = minor. 0 = ok. Vibration: 1 = critical. 2 = significant. 3 = minor. 4 = ok. Missing data returns yellow highlighted cell. | The actual condition of the condition indicator. On a scale of 0 (Poor) thru 4 (Excellent). Blank = No input. 0 = Level 0 (Poor). 1 = Level 1 (Abnormal). 2 = Level 2 (Unusual). 3 = Level 3 (Acceptable). 4 = Level 4 (Excellent). Missing data returns yellow highlighted cell.
[10 empty] | Insert Asset Acquired Date in the following format: mm/dd/yy |  | Insert Estimated Life as a number in years. | If "0" weighting in column (D) is entered = N/A. | This value for the Overall Asset Health Index is used to trigger flags when it is reached and to provide an "Intervention" output for other program use.
Date of Record: | 2014-10-27 14:30 | Asset Health Matrix for | PETE 2 Boiler Waterwalls |  |  |  | Serial No. |  |  | Asset Acquired |  | Estimated Life (yrs) | 40 | 40 | Overall AHI Poor Health Set Point | Sum | Level 0 Forcing | Level 1 Forcing | Sum | Max CF | Pool 100 | Forcing Trigger |  |  |  |  | Health Risk Outputs
Rev 1. Oct 2014 |  |  | (1 - 10) |  | (0 - 4) |  |  |  | Individual CI Health |  |  |  | Individual CI Health Monitor | Notes |  | 240.678 | 0.6 | 0.3 | 447.4576 | 4 | 100 | 8 | Error Reporting |  | 15 | 15 | 0 | 0 | 3
Technology or Procedure | Condition Indicator (CI) | Failure Mode (s) | Failure Mode Impact Weighting | Test Result Data | CI "Normalized" Condition Factor (CF) |  | Level 4 | Level 3 | Level 2 | Level 1 | Level 0 | (Critical CI) Low Asset Health Alert |  |  |  | CI score | Calc for Level 1 & 0 Forcing | Switch for Level 1 & 0 Forcing | Total Max | Max CI score | Weighting (Auto) | Weighting adjustment | Is Column "F" blank | CF entry errors | Confidence Factor |  | Individual CI's Health Risk flagged = 1 | AHI Intervention flagged =1 | CI Health Monitor flagged = 1 | Original FM Weightings
Re-name or assign Technology or Procedure categories | Insert all Relevant CI's for this Asset | Provide brief Failure Mode description for each CI | Assign FM Weighting - use table below for reference | Used only for actual condition data from a 3rd party program | Assign CI Factor only if asset is currently being assessed | Enter "X" if CI requires assigning to tables below | [7 empty] | This section is for AM and / or the user to add notes if deemed to be useful.
Ultrasonic Thickness | Sootblower Panel Wall Thickness | Tube Wall Thinning | 8 | - | 1 |  |  |  |  | Abnormal |  | Asset Health Risk | 25% |  |  | 8.4746 | 2.4 | 1 | 81.3559 | 33.8983 | 8.4746 | 15 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 3
| Burner Corner Tube Wall Thickness | Tube Wall Thinning | 8 | - | 2 |  |  |  | Unusual |  |  | N/A | 50% |  |  | 16.9492 | 1 | 1 | 33.8983 | 33.8983 | 8.4746 | 15 | 1 | 0 | 1 | 1 | 0 |  | 0 | 3
| Tubes Below SOFA Wall Thickness | Tube Wall Thinning | 8 | - | 2 |  |  |  | Unusual |  |  | N/A | 50% |  |  | 16.9492 | 1 | 1 | 33.8983 | 33.8983 | 8.4746 | 15 | 1 | 0 | 1 | 1 | 0 |  | 0 | 0
Visual Examination | Flat Spotting | Tube Wall Thinning | 6 | - | 1 |  |  |  |  | Abnormal |  | N/A | 25% |  |  | 3.9548 | 1 | 0 | 15.8192 | 15.8192 | 3.9548 | 7 | 1 | 0 | 1 | 1 | 0 |  | 1 | 5
| Excessive Ash Buildup | Ash on Tubing | 3 | - | 1 |  |  |  |  | Abnormal |  | N/A | 25% |  |  | 1.6949 | 1 | 0 | 6.7797 | 6.7797 | 1.6949 | 3 | 1 | 0 | 1 | 1 | 0 |  | 1 | 5
| Transverse Cracking/Alligator Hide | Thermal Fatigue/Fireside Corrosion | 5 | - | 4 |  | Excellent |  |  |  |  | N/A | 100% |  |  | 11.2994 | 1 | 0 | 11.2994 | 11.2994 | 2.8249 | 5 | 1 | 0 | 1 | 1 | 0 |  | 0 | 5
Metallurgical Evaluation (Destructive Examination) | Outside Diameter | Tube Wall Thinning | 8 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 25.4237 | 1 | 1 | 33.8983 | 33.8983 | 8.4746 | 15 | 1 | 0 | 1 | 1 | 0 |  | 0 | 7
| Inside Diameter | Tube Wall Thinning | 8 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 25.4237 | 1 | 1 | 33.8983 | 33.8983 | 8.4746 | 15 | 1 | 0 | 1 | 1 | 0 |  | 0 | 7
| Tube Wall Thickness | Tube Wall Thinning | 8 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 25.4237 | 1 | 1 | 33.8983 | 33.8983 | 8.4746 | 15 | 1 | 0 | 1 | 1 | 0 |  | 0 | 7
| Deposit Weight Density | Buildup of Waterside Impurities | 5 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 8.4746 | 1 | 0 | 11.2994 | 11.2994 | 2.8249 | 5 | 1 | 0 | 1 | 1 | 0 |  | 0 | 8
| Material Grade | Correct vs. Incorrect Material | 3 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 5.0847 | 1 | 0 | 6.7797 | 6.7797 | 1.6949 | 3 | 1 | 0 | 1 | 1 | 0 |  | 0 | 7
| Hardness | Material Integrity | 6 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 11.8644 | 1 | 0 | 15.8192 | 15.8192 | 3.9548 | 7 | 1 | 0 | 1 | 1 | 0 |  | 0 | 8
| Microstructure | Material Integrity | 6 | - | 3 | x |  | Acceptable |  |  |  | N/A | 75% |  |  | 11.8644 | 1 | 0 | 15.8192 | 15.8192 | 3.9548 | 7 | 1 | 0 | 1 | 1 | 0 |  | 0 | 8
Failure Analysis Curves | Tube Probability of Failure | Tube Wall Thinning | 0 | 0.01 |  | x | [5 empty] | N/A | N/A |  |  | - | 1 | 0 | - | - | - | - | 0 | Enter CF # | 0 | 0 | 0 |  | 0 | 4
Lagging Indicators | Boiler Tube Failure | Lost Generation | 10 | - | 2 |  |  |  | Unusual |  |  | N/A | 50% |  |  | 33.8983 | 1 | 1 | 67.7966 | 67.7966 | 16.9492 | 30 | 1 | 0 | 1 | 1 | 0 |  | 0 | 0
Cognizant Personnel | Subject Matter Expert Evaluation | Overall Boiler Experience | 9 | - | 3 |  |  | Acceptable |  |  |  | N/A | 75% |  |  | 33.8983 | 1 | 1 | 45.1977 | 45.1977 | 11.2994 | 20 | 1 | 0 | 1 | 1 | 0 |  | 0 | 0
Asset Health Index/Residual Life Factors | 10% | 15% | 20% | 25% | 30% |  | 35% | 0 |  | Overall Asset Health Index | 53.7879 | % | Potential Useful Life Lost |  | If Overall Asset Health Index is highlighted Red, Intervention is required.
Residual Life Factors | 0.2 | 0.25 | 0.3 | 0.35 | 0.4 |  | 0.45 |  |  | Data Availability (Confidence Factor) | 100 | % | Info Reqd. | %
0.6 | [9 empty] | Projected Remaining Useful Life | Info Reqd. | Yrs | Info Reqd. | yrs
40% | 50% | 60% | 70% | 80% | 90% |  | 100%
0.5 | 0.6 | 0.7 | 0.8 | 0.9 | 0.95 |  | 1 | 0 | [5 empty] | Max Value
| 0.6 | [6 empty] | 1 |  |  |  |  | 53.7879 | 100
Current Asset Health Index | 53.7879 | [11 empty] | Donut | Needle
Physical Life Consumed | 285% | 114 | Years | [9 empty] | 180 | 0 | 0
Remaining Physical Life | -185% | -74 | Years | [9 empty] | 45 | 0.11872 | 0.99293
Estimated Useful Life Remaining | -111% | -44.4 | Years | [9 empty] | 45 | 0 | 0
Current Date | 2014-10-27 14:30 | Original Estimated Total Life | 40 | [9 empty] | 45 | Health Threshold
Asset Acquired | 0 | [11 empty] | 45 | 0 | 0
[14 empty] | -0.30902 | 0.95106
[14 empty] | 0 | 0
C.I. Normalized Condition Factors | Description | Normalized Condition Factors Definition
0 | Poor | Condition is bad, prompt repair/rectification is required, operation is not advised.
1 | Abnormal | Possible early signs of a failure that requires repair/rectification at earliest opportunity.
2 | Unusual | Not typical but does not necessarily indicate a possible failure, extra monitoring warranted, repair/rectification at convenient opportunity.
3 | Acceptable | Includes everyday wear and tear and other minor incidents that are viewed as not unusual.
4 | Excellent | Equipment in top condition, with insignificant wear and tear.
Failure Mode Impact Weighting 1 = Low, 10 = High | Description | Severity or Effect Definition
10 | Highest | Failure Severity: Catastrophic, asset becomes inoperable, the failure may result complete unsafe operation and possible fatalities. Significant financial loss or irreversible severe environmental damage that violates law or regulation.
Influence on total asset health: Has the highest impact, important data necessary for determining the most reliable, efficient and safe operation.
9 | Extremely High | Failure Severity: Large reduction in safety margin, asset becomes inoperable; failure may result in LTI's or recordables or reversible environmental damage causing a violation of law or regulation.
Influence on total asset health: Would have an extremely high impact, important data necessary for determining high levels of reliability, efficiency and safety.
8 | Very High | Failure Severity: Failure renders the asset inoperable or unfit for use, reduces the capability of the system or the operators to cope with adverse operating conditions to the extent that there would be significant reduction in safety margin or functional capability.
Influence on total asset health: Would have a very high impact on reliability or for the asset to operate safely, efficiently or correctly.
7 | High | Failure Severity: Has the potential to cause the asset to be inoperable temporarily, causes significant increase in operator workload, causes significant customer dissatisfaction.
Influence on total asset health: Would have a high impact on reliability or for the asset to operate safely, efficiently or correctly.
6 | Moderate | Failure Severity: Failure results in a subsystem or partial malfunction of the asset, reduction in safety margins, conditions impairing operator efficiency or creating significant discomfort.
Influence on total asset health: Would have a moderate impact on reliability or for the asset to operate safely, efficiently or correctly.
5 | Low | Failure Severity: Failure creates enough of a performance loss to cause light damage or minor injuries and possible customer complaints; slight reduction in safety margin or functional capabilities.
Influence on total asset health: Would have a low impact on reliability or for the asset to operate safely, efficiently or correctly.
4 | Very Low | Failure Severity: Failure can be overcome with modifications to the process or asset, but there is minor performance loss.
Influence on total asset health: Would have a very low impact on reliability or for the asset to operate safely, efficiently or correctly.
3 | Minor | Failure Severity: Failure would create a minor nuisance which can be overcome without performance loss.
Influence on total asset health: Would have a minor impact on reliability or for the asset to operate safely, efficiently or correctly.
2 | Very Minor | Failure Severity: Very minor, no damage, no injuries, only results in a maintenance action (only noticed by discriminating customers)
Influence on total asset health: Contributes to minor improvements in reliability, efficiency or safety.
1 | Negligible | Failure Severity: No relevant effect on reliability or safety.
Influence on total asset health: Only minimal effect on improvements in reliability, efficiency or safety.
Assign Failure Mode Impact Weightings 1 = Low, 10 = High | Chose the Condition Indicator Factor that best describes actual equipment condition | C.I. Normalized Condition Factors 0 = Poor , 4 = Excellent | Waterwall Condition Indicators
"0" = omit from AHI | Enter one number (0 - 4) | (0 - 4)
6 |  |  | Flat Spotting / Wear
6 | 1 | 0 | Major erosion or flat spotting which is visually detectable and has defined/sharp edges when felt with the bare hand. Typically the affected areas will be around the burner corners or retractable wall blowers.
|  | 1 | Major erosion or flat spotting which is visually detectable, but has soft edges when felt with the bare hand.
|  | 2 | Moderate erosion or flat spotting which can be visually detected.
|  | 3 | Minor erosion or flat spotting which cannot be visually detected, but can be felt with the bare hand.
|  | 4 | No visually detectable erosion or flat spotting.
3 |  |  | Excessive Ash Buildup
3 | 1 | 0 | Large ash accumulation on tubing like in the two lines below, but is widespread throughout the furnace waterwalls and includes larger hanging clinkers. This type of ash usually bridges over retractable waterwall sootblowers.
|  | 1 | Large sheets of ash accumulation that have a black onyx glass like look to them. These sheets of slag are not easily removed from the wall and are incredibly dense.
|  | 1 | Thick ash accumulation on tubing that consists of three layers: outer layer - hard, brittle, porous layer that makes up the bulk of the deposit / intermediate layer - fused and semi-glossy ash / inner layer - hard, black, and glossy layer. When removed via a tool or blasting this ash should reveal tubing that appears to have been grooved. (grand canyon)
|  | 2 | Thick ash accumulation on tubing that consists of three layers: outer layer - hard, brittle, porous layer that makes up the bulk of the deposit / intermediate layer - white and chalky consistency / inner layer - hard, black, and glossy layer. When removed via a tool or blasting this ash should not reveal any damage to the tubing below.
|  | 3 | Slight ash accumulation on tubing that has a reddish/gray hue to it. This ash is somewhat easily removed with a gloved hand and it comes off in uniformly colored sheets.
|  | 4 | Little to no ash accumulation on tubing. If there is slight accumulation it is easily removed with the brush of a gloved hand.
5 |  |  | Thermal Fatigue/Transverse Cracking
5 | 4 | 0 | Severe transvers or axial cracking found on the tubing. This damage will be widespread in the furnace and it extends deeper into the tubing than a light tigerpaw disc can buff out. The tubing will have an elephant trunk-like appearance with very distinct peaks and valleys.
|  | 1 | Moderate transverse or axial cracking found on the tubing. This damage will be widespread in the furnace and it extends deeper into the tubing than a light tigerpaw disc can buff out. The tubing will have an elephant hide-like appearance with evident plateaus and valleys.
|  | 2 | Moderate transverse or axial cracking found on the tubing. This damage will be more widespread in the furnace, but it is still superficial in nature. The tubing at this stage will have very faint lines covering the crown of the tubing and does not extend into the membrane and/or attachments.
|  | 3 | Minor transverse cracking found on the tubing. This damage will be isolated to a small area and is superficial in nature. It can be easily buffed out with light tigerpaw disc.
|  | 4 | No visually detectable cracking on the tubing.
8 |  |  | Destructive Examination - Outside Diameter
8 | 3 | 0 | Correct material type for application, < 50% of design MWT, DWD greater than 30 gr/ft2, severe pitting on the ID of the tubing, early stages of softening, and final stage of creep.
|  | 1 | Correct material type for application, 50% < x <65% of design MWT, DWD below 30 gr/ft2, moderate to severe pitting on the ID of the tubing, early stages of softening, and moderate stage of creep.
|  | 2 | Correct material type for application, 65% < x < 75% of the design MWT, DWD below 25 gr/ft2, moderate pitting on the ID of the tubing, acceptable hardness, and early stage of creep.
|  | 3 | Correct material type for application, 75% < x < 90% of the design MWT, DWD below 20 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
|  | 4 | Correct material type for application, 90% or greater of the design MWT, DWD below 15 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
8 |  |  | Destructive Examination - Inside Diameter
8 | 3 | 0 | Correct material type for application, < 50% of design MWT, DWD greater than 30 gr/ft2, severe pitting on the ID of the tubing, early stages of softening, and final stage of creep.
|  | 1 | Correct material type for application, 50% < x <65% of design MWT, DWD below 30 gr/ft2, moderate to severe pitting on the ID of the tubing, early stages of softening, and moderate stage of creep.
|  | 2 | Correct material type for application, 65% < x < 75% of the design MWT, DWD below 25 gr/ft2, moderate pitting on the ID of the tubing, acceptable hardness, and early stage of creep.
|  | 3 | Correct material type for application, 75% < x < 90% of the design MWT, DWD below 20 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
|  | 4 | Correct material type for application, 90% or greater of the design MWT, DWD below 15 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
8 |  |  | Destructive Examination - Tube Wall Thickness
8 | 3 | 0 | Correct material type for application, < 50% of design MWT, DWD greater than 30 gr/ft2, severe pitting on the ID of the tubing, early stages of softening, and final stage of creep.
|  | 1 | Correct material type for application, 50% < x <65% of design MWT, DWD below 30 gr/ft2, moderate to severe pitting on the ID of the tubing, early stages of softening, and moderate stage of creep.
|  | 2 | Correct material type for application, 65% < x < 75% of the design MWT, DWD below 25 gr/ft2, moderate pitting on the ID of the tubing, acceptable hardness, and early stage of creep.
|  | 3 | Correct material type for application, 75% < x < 90% of the design MWT, DWD below 20 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
|  | 4 | Correct material type for application, 90% or greater of the design MWT, DWD below 15 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
5 |  |  | Destructive Examination - Deposit Weight Density
5 | 3 | 0 | Correct material type for application, < 50% of design MWT, DWD greater than 30 gr/ft2, severe pitting on the ID of the tubing, early stages of softening, and final stage of creep.
|  | 1 | Correct material type for application, 50% < x <65% of design MWT, DWD below 30 gr/ft2, moderate to severe pitting on the ID of the tubing, early stages of softening, and moderate stage of creep.
|  | 2 | Correct material type for application, 65% < x < 75% of the design MWT, DWD below 25 gr/ft2, moderate pitting on the ID of the tubing, acceptable hardness, and early stage of creep.
|  | 3 | Correct material type for application, 75% < x < 90% of the design MWT, DWD below 20 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
|  | 4 | Correct material type for application, 90% or greater of the design MWT, DWD below 15 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
3 |  |  | Destructive Examination - Material Grade
3 | 3 | 0 | Correct material type for application, < 50% of design MWT, DWD greater than 30 gr/ft2, severe pitting on the ID of the tubing, early stages of softening, and final stage of creep.
|  | 1 | Correct material type for application, 50% < x <65% of design MWT, DWD below 30 gr/ft2, moderate to severe pitting on the ID of the tubing, early stages of softening, and moderate stage of creep.
|  | 2 | Correct material type for application, 65% < x < 75% of the design MWT, DWD below 25 gr/ft2, moderate pitting on the ID of the tubing, acceptable hardness, and early stage of creep.
|  | 3 | Correct material type for application, 75% < x < 90% of the design MWT, DWD below 20 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
|  | 4 | Correct material type for application, 90% or greater of the design MWT, DWD below 15 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
6 |  |  | Destructive Examination - Hardness
6 | 3 | 0 | Correct material type for application, < 50% of design MWT, DWD greater than 30 gr/ft2, severe pitting on the ID of the tubing, early stages of softening, and final stage of creep.
|  | 1 | Correct material type for application, 50% < x <65% of design MWT, DWD below 30 gr/ft2, moderate to severe pitting on the ID of the tubing, early stages of softening, and moderate stage of creep.
|  | 2 | Correct material type for application, 65% < x < 75% of the design MWT, DWD below 25 gr/ft2, moderate pitting on the ID of the tubing, acceptable hardness, and early stage of creep.
|  | 3 | Correct material type for application, 75% < x < 90% of the design MWT, DWD below 20 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
|  | 4 | Correct material type for application, 90% or greater of the design MWT, DWD below 15 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
6 |  |  | Destructive Examination - Microstructure
6 | 3 | 0 | Correct material type for application, < 50% of design MWT, DWD greater than 30 gr/ft2, severe pitting on the ID of the tubing, early stages of softening, and final stage of creep.
|  | 1 | Correct material type for application, 50% < x <65% of design MWT, DWD below 30 gr/ft2, moderate to severe pitting on the ID of the tubing, early stages of softening, and moderate stage of creep.
|  | 2 | Correct material type for application, 65% < x < 75% of the design MWT, DWD below 25 gr/ft2, moderate pitting on the ID of the tubing, acceptable hardness, and early stage of creep.
|  | 3 | Correct material type for application, 75% < x < 90% of the design MWT, DWD below 20 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
|  | 4 | Correct material type for application, 90% or greater of the design MWT, DWD below 15 gr/ft2, minor pitting if any on the ID of the tubing, acceptable hardness, and no signs of creep.
8 |  |  | Wall Thickness - Sootblower Panel
8 | 1 | 0 | More than 25% of tubing is < 50% of the design MWT.
|  | 1 | More than 25% of tubing is below the calculated minimum wall thickness.
|  | 1 | Majority of tubing is 50% < x < 65% of the design MWT.
|  | 2 | Majority of tubing is 65% < x < 75% of the design MWT.
|  | 3 | Majority of tubing is 75% < x < 90% of the design MWT.
|  | 4 | 90% or greater of the design MWT.
8 |  |  | Wall Thickness - Burner Corner Tube
8 | 1 | 0 | More than 25% of tubing is < 50% of the design MWT.
|  | 1 | More than 25% of tubing is below the calculated minimum wall thickness.
|  | 1 | Majority of tubing is 50% < x < 65% of the design MWT.
|  | 2 | Majority of tubing is 65% < x < 75% of the design MWT.
|  | 3 | Majority of tubing is 75% < x < 90% of the design MWT.
|  | 4 | 90% or greater of the design MWT.
8 |  |  | Wall Thickness - Tubes Below SOFA
8 | 2 | 0 | More than 25% of tubing is < 50% of the design MWT.
|  | 1 | More than 25% of tubing is below the calculated minimum wall thickness.
|  | 1 | Majority of tubing is 50% < x < 65% of the design MWT.
|  | 2 | Majority of tubing is 65% < x < 75% of the design MWT.
|  | 3 | Majority of tubing is 75% < x < 90% of the design MWT.
|  | 4 | 90% or greater of the design MWT.
10 |  |  | Boiler Tube Failures
10 | 2 | 0 | Greater than 5 boiler tube failures in the past 6 months and in various locations.
|  | 1 | 3 < x < 5 boiler tube failures in the past 12 months.
|  | 2 | 1 < x < 3 boiler tube failures in the past 12 months.
|  | 3 | No boiler tube failures in the past 12 months or one boiler tube failure in the past 24 months.
|  | 4 | No boiler tube failures in the past 24 months.
10 |  |  | Probability of Failure Curve Analysis
0 | 1 | Probability of failure input from analysis tool. (From Matrix above) | Level 0 = 85% thru 100% probability of Failure |  |  |  | 85% | 0.6 | 0 | 100%
|  |  | Level 1 = 66% thru 84% probability of Failure |  |  |  | 66% | 1.36 | 0.64 | 84%
|  | 1% | Level 2 = 26% thru 65% probability of Failure |  |  |  | 26% | 2.96 | 1.4 | 65%
|  |  | Level 3 = 3% thru 25% probability of Failure |  |  |  | 3% | 3.88 | 3 | 25%
|  |  | Level 4 = 0% thru 2% probability of Failure |  |  |  | 0% | 4 | 3.92 | 2%
50%
0% 100%
Asset Health Meter
Sum score = sum of scores from all submitted C.I's. Overall Asset Health Index = sum score / max score. <25. 25-50. 50-75. >75. Data availability = max score / max possible score. <60. 60-80. >80. When data availability falls below 75% = Consider Collecting More Data When any condition indicator has a "0" score = 1 or more CI in Poor Health When the projected asset life loss is >25% = Estimated > 1/4 Asset Life Lost
Note on I9: Russ: Enter Serial Number if this asset may be rotated with other identical assets, (spares, unit 1 to unit 2 etc.)
Note on L9: Russ: Enter the date this asset was first put into service - m/dd/yy
Note on N9: Russ: Enter the estimated life expectancy from first operating date.
Note on O9: Russ Cochran: Insert the minimum acceptable value for the Overall Asset Health Index, below this value the AHI will be flagged and an Intervention output is generated.